## Slide 1: Architectural Linear
RC - TM suspended, surface and wall
TruGroove Micro
!
ATTENTION: Install in accordance with national and local building and electrical codes.
Module Lengths
TruGroove suspended, surface and wall micro versions are available in the lengths listed on the right.
Dimensions here are overall length, not including endcaps.
Endcaps
Overall row lengths do not include endcaps. Add two endcaps to the overall length of each row.
Indirect
Direct
Direct/Indirect
Row configurations
The nominal 2, 2.5, 3, 3.5, 4, 5, 6 and 8ft modules can be combined to create continuous rows of various lengths in 6in increments. There may be multiple ways to make up a specific row length. Modules can be combined in any order; use the following guidelines to optimize your row configuration:
To optimize a row for best price
Build the row with mostly longer module lengths. See example below:
To optimize a row for best aesthetic appearance
Use modules in a pattern to ensure mounting points are symmetric in the run. See example below:
To optimize a row for installation condition
Choose modules lengths that allow mounting points to avoid obstacles such as sprinkler heads & HVAC vents. See example below:
6ft
6ft
6ft
8ft
8ft
2ft
8ft
6ft
4ft

## Slide 2: Row Configurations
!
ATTENTION: Install in accordance with national and local building and electrical codes.
Lens Only Module Lengths
TruGroove suspended, surface and wall micro versions with lenses only are available in the lengths listed on the right.*
Louver Only Module Lengths
TruGroove suspended, surface and wall micro versions with louvers only are available in the lengths listed on the right.*
Lens/Louver Combo Lengths
TruGroove suspended, surface and wall micro versions with combination lens and louver are available in the lengths ≥ 4ft as listed on the right.* Louver length: 6in or 1ft
Louver position: one end or both ends
RC-TM
4ft
5ft
6ft
8ft
4ft
5ft
6ft
8ft
Lens Module Lengths with Sensor
TruGroove suspended, surface and wall micro versions with lens and sensors are available in the lengths listed on the right. Suspended and surface fixtures can be rotated 180˚. Wall fixtures are mounted on the wall, with sensors placed on the left end.*
Louver Module Lengths with Sensor
TruGroove suspended, surface and wall micro versions are available with louvers and sensors in the lengths listed on the right. Suspended and surface fixtures can be rotated 180˚. Wall fixtures are mounted on the wall, with sensors placed on the left end.*
2ft
2.5ft
3ft
4ft
5ft
6ft
8ft
3.5ft
Bottom view of fixtures
Bottom view of fixtures
Bottom view of fixtures
Bottom view of fixtures
Bottom view of fixtures
*Dimensions are overall fixture lengths, not including endcaps.
www.ledalite.com

## Slide 3: Row Configurations
Suspended Mount Spacing
Suspended sling mount brackets attach at run ends and joints. For on-grid T-bar ceiling installations, mounts attach directly to T-Bar. Mounting options are available for off-grid T-bar installations, non-accessible ceilings and a wide variety of other ceiling types.
!
ATTENTION: Install in accordance with national and local building and electrical codes.
Surface Mount Spacing
Surface mounting studs should be located close to ends of modules within range specified below.
Wall Mount Spacing
Variable wall mount brackets can be positioned within 12” of module end or joint. Maximum distance between wall mounts is 48”.
RC-TM
www.ledalite.com
Power Feed
Power for the entire row can be placed at either end or any joint. See examples below.

## Slide 4: Row Configurations
Battery Pack (BP)
Select modules are available with an optional Battery Pack which will power the entire length of a module.
www.ledalite.com
RC-TM
!
ATTENTION: Install in accordance with national and local building and electrical codes.
Suspended & Wall: Direct/Indirect or Indirect/Direct - BP Availability
Module lengths of ≥ 6ft are available with an optional Battery Pack which will power the entire length of the direct hemisphere.
Suspended, Surface & Wall: Direct - BP Availability
Module lengths of ≥ 4ft are available with an optional Battery Pack which will power the entire length of the direct hemisphere.
Suspended & Wall: Indirect - BP Availability
Module lengths of ≥4ft are available with an optional Battery Pack which will power the entire length of the indirect hemisphere.
Side view of fixtures
Side view of fixtures
Side view of fixtures

## Slide 5: Row Configurations
RC-TM
Sensors in Rows
www.ledalite.com
!
ATTENTION: Install in accordance with national and local building and electrical codes.
Single Sensor Controlling Whole Row
Purple & brown (or purple & grey/pink) control wires MUST be connected between fixtures.
  Note:
  A maximum of 8 drivers can be wired to one sensor; confirm fixture driver count with factory.
Sensor
8ft
4ft
1
Bottom view of fixtures
Multiple Sensors Controlling Separate Zones in a Row
Purple & brown (or purple & grey/pink) control wires MUST NOT be connected between zones.
  Notes:
  A maximum of 8 drivers can be wired to one sensor; confirm fixture driver count with factory.
  Only one sensor is allowed on a wired zone. (Sensors can be paired together wirelessly via a mobile app).
Sensor
8ft
4ft
2
Bottom view of fixtures
Sensor
Zone 2
Zone 1
8ft
4ft
Bottom view of fixtures
Sensor
Sensors are too close together for proper operation.
Sensors are at minimum required distance for correct operation.
Sensors are at a maximum distance of 40ft apart.
Sensor
40ft Max.
Sensor
Sensor
Sensor Spacing
For correct operation, sensors should be placed a minimum distance of 8ft apart.
Wireless sensors should be placed no further than 40ft apart for good wireless signal connection.
Important Consideration When Using Sensors in a Row
For fixtures with wireless sensors (CS, SB or RA options):
  DO NOT connect fixture purple & brown (or purple & grey/pink) control wires to an external dimming switch.
  Fixture mains wiring should not be connected to a circuit with an external on/off switch.
For best aesthetic condition, place sensors at ends of row only so as not to break the continuous lens.
For better occupancy coverage in longer rows, sensors may be placed mid run, but keep in mind this will break the continuous lens into discrete sections.
Sensor
8ft
4ft
Bottom view of fixtures
Sensor
Zone 2
Zone 1
Bottom view of fixtures

## Slide 6: Row Configurations
RC-TM
Daylight sensor The light sensor measures the total amount of light in a circular field of approximately 80% of the PIR detection area. The following aspects should be observed during installation:
• Minimum distance from the window ≥2ft (0.6m).
• Prevent light reflections from outside entering the sensor (for example sunlight reflection on a car hood) as this will lead to incorrect light regulation.
As a guideline the formula 0.72 x H can be used to calculate the minimum distance between the window and sensor whereby H is the height from the bottom of the window to the sensor.
Occupancy Sensor Coverage:
Note: Longer dimension of detection area (Y1, Y2) is parallel to longer dimension of the luminaire.
The detection area for the movement sensor can be roughly divided into two parts:
• Minor movement (person moving ≤3ft/s or 0.9m/s).
• Major movement (person moving ≥3ft/s or 0.9m/s).
Photosensor spatial response
!
ATTENTION: Install in accordance with national and local building and electrical codes.
www.ledalite.com